## 00000
Loop id: KA HB 8 04 00000
| Manufacture | Type | Description | Certficate | Authority | Ui [V] | li [mA] | Pi [mW] | Ri [Ώ] | Ci [nF] | Li [mH]
TRANSMITTER DATA | Endress+Hauser | DC11TEN + FEC12 | 2-Wire Transmitter | KEMA 97ATEX4493 | KEMA | 30 | 120 | 1000 |  | 0 | 0
| Endress+Hauser | RIA 261 | Dig. Process Indicator | DMT 01 ATEX E 036 | DMT | 30 | 150 | 750 |  | 0 | 0
Ui x Ii
| Manufacture | Type | Description | Certficate | Authority | Uo [V] | lo [mA] | Po [mW] | Ro [Ώ] | Co [nF] | Lo [mH]
BARRIER DATA | R. STAHL | 9461/12-08-11/ -21 | Analog Input | PTB 99 ATEX 2175 | PTB | 26.2 | 91 | 591 |  | 44 | 2
[10 empty] | 58 | 1
[10 empty] | 73 | 0.5
[10 empty] | 97 | 0.2
CABLE DATA | Manufacture: | Coferro | Wires: |  | 2 |  |  | lo ≤ li(min) |  |  | OK
| Type: | YSLCY-OZ/JZ | Size [mm2]: |  | 0.5 |  |  | Vo ≤ Vi(min) |  |  | OK
| Description: | Instrument cable | Max Length, Lmax [m]: |  | 320 |  |  | Po ≤ Pi(min) |  |  | OK
|  |  | Capacitance Core/Core, Ci [nF/km] |  | 135
|  |  | Capacitance Core/Braid, Ci [nF/km] |  | 185 |  |  | Ci(tot) [nF] |  |  | 72.8
|  |  | Inductance, Li [mH/km]: |  | 0.65 |  |  | Li(tot) [mH] |  |  | 0.208
|  |  | Resistance [Ώkm/wire]: |  | 39
|  |  | The circuit is approved for gas group: IIC |  |  |  |  | "(min)" er laveste værdi af instru-
menterne i transmitter data
Ui [V] | Maximum voltage that can be applied to the intrinsically safe circuits.
li [mA] | Maximum current that can be applied to the intrinsically safe circuits.
Pi [mW] | Maximum input power in an intrinsically safe circuit that can be dissipated without invalidating intrinsic safety.
Ri [Ώ] | Resistance in the intrinsically safe circuits.
Ci [nF] | Total equivalent internal capacitance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Li [mH] | Total equivalent internal inductance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Uo [V] | Maximun output voltage in an intrinsically safe circuit that can appear under open-circuit conditions.
lo [mA] | Maximum current in an intrinsically safe circuit that can be taken from the connection facilities.
Po [mW] | Maximum electrical power in an intrinsically safe circuit that can be taken from the apparatus.
Ro [Ώ] | Maximum load resistance.
Co [nF] | Maximum capitance in an intrinsically safe circuit that can be connected to the connection facilities.
Lo [mH] | Maximum inductance in an intrinsically safe circuit that can be connected to the connection facilities.

## Tavledok
Loop id: Tavledok
| Manufacture | Type | Description | Certficate | Authority | Ui [V] | li [mA] | Pi [mW] | Ri [Ώ] | Ci [nF] | Li [mH]
TRANSMITTER DATA | ifm electronic GmbH | SF 311 A | Flowswitch | DMT 03 ATEX E 090 X | DMT | 16 | 100 | 680 |  | 1.2 | 0.006
| Manufacture | Type | Description | Certficate | Authority | Uo [V] | lo [mA] | Po [mW] | Ro [Ώ] | Co [nF] | Lo [mH]
BARRIER DATA | ifm electronic GmbH | SN 2301 | N/A | PTB 01 ATEX 2075 | PTB | 15.8 | 92 | 680 |  | 185 | 1
CABLE DATA | Manufacture: | Coferro | Wires: |  | 5 |  |  | lo ≤ li(min) |  |  | OK
| Type: | YSLCY-OZ/JZ | Size [mm2]: |  | 0.5 |  |  | Vo ≤ Vi(min) |  |  | OK
| Description: | Instrument cable | Max Length, Lmax [m]: |  | 807 |  |  | Po ≤ Pi(min) |  |  | OK
|  |  | Capacitance Core/Core, Ci [nF/km] |  | 135
|  |  | Capacitance Core/Braid, Ci [nF/km] |  | 185 |  |  | Ci(tot) [nF] |  |  | 184.7925
|  |  | Inductance, Li [mH/km]: |  | 0.65 |  |  | Li(tot) [mH] |  |  | 0.53055
|  |  | Resistance [Ώkm/wire]: |  | 39
|  |  | The circuit is approved for gas group: IIC |  |  |  |  | "(min)" er laveste værdi af instru-
menterne i transmitter data
Ui [V] | Maximum voltage that can be applied to the intrinsically safe circuits.
li [mA] | Maximum current that can be applied to the intrinsically safe circuits.
Pi [mW] | Maximum input power in an intrinsically safe circuit that can be dissipated without invalidating intrinsic safety.
Ri [Ώ] | Resistance in the intrinsically safe circuits.
Ci [nF] | Total equivalent internal capacitance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Li [mH] | Total equivalent internal inductance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Uo [V] | Maximun output voltage in an intrinsically safe circuit that can appear under open-circuit conditions.
lo [mA] | Maximum current in an intrinsically safe circuit that can be taken from the connection facilities.
Po [mW] | Maximum electrical power in an intrinsically safe circuit that can be taken from the apparatus.
Ro [Ώ] | Maximum load resistance.
Co [nF] | Maximum capitance in an intrinsically safe circuit that can be connected to the connection facilities.
Lo [mH] | Maximum inductance in an intrinsically safe circuit that can be connected to the connection facilities.

## 00801
Loop id: KA HB 8 04 00801
| Manufacture | Type | Description | Certficate | Authority | Ui [V] | li [mA] | Pi [mW] | Ri [Ώ] | Ci [nF] | Li [mH]
TRANSMITTER DATA | Pepperl + Fuchs GmbH | NCN15 el. NCB2 | Induktiv aftaster | PTB 00 ATEX 2048 X | PTB | 16 | 25 | 64 |  | 110 | 0.1
| Manufacture | Type | Description | Certficate | Authority | Uo [V] | lo [mA] | Po [mW] | Ro [Ώ] | Co [nF] | Lo [mH]
BARRIER DATA | R. STAHL | 9470/22-16-11 | Digital Input | PTB 99 ATEX 2184 | PTB | 11.6 | 22 | 51 |  | 100 | 50
[10 empty] | 200 | 20
[10 empty] | 280 | 10
[10 empty] | 350 | 5
[10 empty] | 480 | 2
[10 empty] | 600 | 1
[10 empty] | 750 | 0.5
CABLE DATA | Manufacture: | Coferro | Wires: |  | 2 |  |  | lo ≤ li(min) |  |  | OK
| Type: | YSLCY-OZ/JZ | Size [mm2]: |  | 0.5 |  |  | Vo ≤ Vi(min) |  |  | OK
| Description: | Instrument cable | Max Length, Lmax [m]: |  | 1626 |  |  | Po ≤ Pi(min) |  |  | OK
|  |  | Capacitance Core/Core, Ci [nF/km] |  | 135
|  |  | Capacitance Core/Braid, Ci [nF/km] |  | 185 |  |  | Ci(tot) [nF] |  |  | 479.915
|  |  | Inductance, Li [mH/km]: |  | 0.65 |  |  | Li(tot) [mH] |  |  | 1.1569
|  |  | Resistance [Ώkm/wire]: |  | 39
|  |  | The circuit is approved for gas group: IIC |  |  |  |  | "(min)" er laveste værdi af instru-
menterne i transmitter data
Ui [V] | Maximum voltage that can be applied to the intrinsically safe circuits.
li [mA] | Maximum current that can be applied to the intrinsically safe circuits.
Pi [mW] | Maximum input power in an intrinsically safe circuit that can be dissipated without invalidating intrinsic safety.
Ri [Ώ] | Resistance in the intrinsically safe circuits.
Ci [nF] | Total equivalent internal capacitance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Li [mH] | Total equivalent internal inductance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Uo [V] | Maximun output voltage in an intrinsically safe circuit that can appear under open-circuit conditions.
lo [mA] | Maximum current in an intrinsically safe circuit that can be taken from the connection facilities.
Po [mW] | Maximum electrical power in an intrinsically safe circuit that can be taken from the apparatus.
Ro [Ώ] | Maximum load resistance.
Co [nF] | Maximum capitance in an intrinsically safe circuit that can be connected to the connection facilities.
Lo [mH] | Maximum inductance in an intrinsically safe circuit that can be connected to the connection facilities.

## 20851
Loop id: KA HB 8 04 20851
| Manufacture | Type | Description | Certficate | Authority | Ui [V] | li [mA] | Pi [mW] | Ri [Ώ] | Ci [nF] | Li [mH]
TRANSMITTER DATA | Micro Motion | 2700I13DEZAZZZ | 2-Wire Transmitter | DMT 01 ATEX E 082 X | DMT | 30 | 300 | 1000 |  | 0 | 0
| Manufacture | Type | Description | Certficate | Authority | Uo [V] | lo [mA] | Po [mW] | Ro [Ώ] | Co [nF] | Lo [mH]
BARRIER DATA | R. STAHL | 9461/12-08-11/ -21 | Analog Input | PTB 99 ATEX 2175 | PTB | 26.2 | 91 | 591 |  | 44 | 2
[10 empty] | 58 | 1
[10 empty] | 73 | 0.5
[10 empty] | 97 | 0.2
CABLE DATA | Manufacture: | Coferro | Wires: |  | 2 |  |  | lo ≤ li(min) |  |  | OK
| Type: | YSLCY-OZ/JZ | Size [mm2]: |  | 0.5 |  |  | Vo ≤ Vi(min) |  |  | OK
| Description: | Instrument cable | Max Length, Lmax [m]: |  | 320 |  |  | Po ≤ Pi(min) |  |  | OK
|  |  | Capacitance Core/Core, Ci [nF/km] |  | 135
|  |  | Capacitance Core/Braid, Ci [nF/km] |  | 185 |  |  | Ci(tot) [nF] |  |  | 72.8
|  |  | Inductance, Li [mH/km]: |  | 0.65 |  |  | Li(tot) [mH] |  |  | 0.208
|  |  | Resistance [Ώkm/wire]: |  | 39
|  |  | The circuit is approved for gas group: IIC |  |  |  |  | "(min)" er laveste værdi af instru-
menterne i transmitter data
Ui [V] | Maximum voltage that can be applied to the intrinsically safe circuits.
li [mA] | Maximum current that can be applied to the intrinsically safe circuits.
Pi [mW] | Maximum input power in an intrinsically safe circuit that can be dissipated without invalidating intrinsic safety.
Ri [Ώ] | Resistance in the intrinsically safe circuits.
Ci [nF] | Total equivalent internal capacitance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Li [mH] | Total equivalent internal inductance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Uo [V] | Maximun output voltage in an intrinsically safe circuit that can appear under open-circuit conditions.
lo [mA] | Maximum current in an intrinsically safe circuit that can be taken from the connection facilities.
Po [mW] | Maximum electrical power in an intrinsically safe circuit that can be taken from the apparatus.
Ro [Ώ] | Maximum load resistance.
Co [nF] | Maximum capitance in an intrinsically safe circuit that can be connected to the connection facilities.
Lo [mH] | Maximum inductance in an intrinsically safe circuit that can be connected to the connection facilities.

## 20852
Loop id: KA HB 8 04 20852
| Manufacture | Type | Description | Certficate | Authority | Ui [V] | li [mA] | Pi [mW] | Ri [Ώ] | Ci [nF] | Li [mH]
TRANSMITTER DATA | Micro Motion | 1700 I 1 3 D E Z A ZZZ | 2-Wire Transmitter | DMT 01 ATEX E 082 X | DMT | 30 | 300 | 1000 |  | 0 | 0
| Manufacture | Type | Description | Certficate | Authority | Uo [V] | lo [mA] | Po [mW] | Ro [Ώ] | Co [nF] | Lo [mH]
BARRIER DATA | R. STAHL | 9461/12-08-11/ -21 | Analog Input | PTB 99 ATEX 2175 | PTB | 26.2 | 91 | 591 |  | 44 | 2
[10 empty] | 58 | 1
[10 empty] | 73 | 0.5
[10 empty] | 97 | 0.2
CABLE DATA | Manufacture: | Coferro | Wires: |  | 2 |  |  | lo ≤ li(min) |  |  | OK
| Type: | YSLCY-OZ/JZ | Size [mm2]: |  | 0.5 |  |  | Vo ≤ Vi(min) |  |  | OK
| Description: | Instrument cable | Max Length, Lmax [m]: |  | 320 |  |  | Po ≤ Pi(min) |  |  | OK
|  |  | Capacitance Core/Core, Ci [nF/km] |  | 135
|  |  | Capacitance Core/Braid, Ci [nF/km] |  | 185 |  |  | Ci(tot) [nF] |  |  | 72.8
|  |  | Inductance, Li [mH/km]: |  | 0.65 |  |  | Li(tot) [mH] |  |  | 0.208
|  |  | Resistance [Ώkm/wire]: |  | 39
|  |  | The circuit is approved for gas group: IIC |  |  |  |  | "(min)" er laveste værdi af instru-
menterne i transmitter data
Ui [V] | Maximum voltage that can be applied to the intrinsically safe circuits.
li [mA] | Maximum current that can be applied to the intrinsically safe circuits.
Pi [mW] | Maximum input power in an intrinsically safe circuit that can be dissipated without invalidating intrinsic safety.
Ri [Ώ] | Resistance in the intrinsically safe circuits.
Ci [nF] | Total equivalent internal capacitance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Li [mH] | Total equivalent internal inductance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Uo [V] | Maximun output voltage in an intrinsically safe circuit that can appear under open-circuit conditions.
lo [mA] | Maximum current in an intrinsically safe circuit that can be taken from the connection facilities.
Po [mW] | Maximum electrical power in an intrinsically safe circuit that can be taken from the apparatus.
Ro [Ώ] | Maximum load resistance.
Co [nF] | Maximum capitance in an intrinsically safe circuit that can be connected to the connection facilities.
Lo [mH] | Maximum inductance in an intrinsically safe circuit that can be connected to the connection facilities.

## 30801 og 40802
Loop id: KA HB 8 04 30801 og 40802
| Manufacture | Type | Description | Certficate | Authority | Ui [V] | li [mA] | Pi [mW] | Ri [Ώ] | Ci [nF] | Li [mH]
TRANSMITTER DATA | ROSEMOUNT INC | 3051* | 2-Wire Transmitter | BAS97ATEX1089X | EECS | 30 | 200 | 900 |  | 12 | 0
| Manufacture | Type | Description | Certficate | Authority | Uo [V] | lo [mA] | Po [mW] | Ro [Ώ] | Co [nF] | Lo [mH]
BARRIER DATA | R. STAHL | 9461/12-08-11/ -21 | Analog Input | PTB 99 ATEX 2175 | PTB | 26.2 | 91 | 591 |  | 44 | 2
[10 empty] | 58 | 1
[10 empty] | 73 | 0.5
[10 empty] | 97 | 0.2
CABLE DATA | Manufacture: | Coferro | Wires: |  | 2 |  |  | lo ≤ li(min) |  |  | OK
| Type: | YSLCY-OZ/JZ | Size [mm2]: |  | 0.5 |  |  | Vo ≤ Vi(min) |  |  | OK
| Description: | Instrument cable | Max Length, Lmax [m]: |  | 307 |  |  | Po ≤ Pi(min) |  |  | OK
|  |  | Capacitance Core/Core, Ci [nF/km] |  | 135
|  |  | Capacitance Core/Braid, Ci [nF/km] |  | 185 |  |  | Ci(tot) [nF] |  |  | 81.8425
|  |  | Inductance, Li [mH/km]: |  | 0.65 |  |  | Li(tot) [mH] |  |  | 0.19955
|  |  | Resistance [Ώkm/wire]: |  | 39
|  |  | The circuit is approved for gas group: IIC |  |  |  |  | "(min)" er laveste værdi af instru-
menterne i transmitter data
Ui [V] | Maximum voltage that can be applied to the intrinsically safe circuits.
li [mA] | Maximum current that can be applied to the intrinsically safe circuits.
Pi [mW] | Maximum input power in an intrinsically safe circuit that can be dissipated without invalidating intrinsic safety.
Ri [Ώ] | Resistance in the intrinsically safe circuits.
Ci [nF] | Total equivalent internal capacitance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Li [mH] | Total equivalent internal inductance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Uo [V] | Maximun output voltage in an intrinsically safe circuit that can appear under open-circuit conditions.
lo [mA] | Maximum current in an intrinsically safe circuit that can be taken from the connection facilities.
Po [mW] | Maximum electrical power in an intrinsically safe circuit that can be taken from the apparatus.
Ro [Ώ] | Maximum load resistance.
Co [nF] | Maximum capitance in an intrinsically safe circuit that can be connected to the connection facilities.
Lo [mH] | Maximum inductance in an intrinsically safe circuit that can be connected to the connection facilities.

## 31801
Loop id: KA HB 8 04 31801
| Manufacture | Type | Description | Certficate | Authority | Ui [V] | li [mA] | Pi [mW] | Ri [Ώ] | Ci [nF] | Li [mH]
TRANSMITTER DATA | Endress+Hauser | DC11TEN + FEC12 | 2-Wire Transmitter | KEMA 97ATEX4493 | KEMA | 30 | 120 | 1000 |  | 0 | 0
| Manufacture | Type | Description | Certficate | Authority | Uo [V] | lo [mA] | Po [mW] | Ro [Ώ] | Co [nF] | Lo [mH]
BARRIER DATA | R. STAHL | 9470/22-16-11 | Digital Input | PTB 99 ATEX 2184 | PTB | 11.6 | 22 | 51 |  | 100 | 50
[10 empty] | 200 | 20
[10 empty] | 280 | 10
[10 empty] | 350 | 5
[10 empty] | 480 | 2
[10 empty] | 600 | 1
[10 empty] | 750 | 0.5
CABLE DATA | Manufacture: | Coferro | Wires: |  | 2 |  |  | lo ≤ li(min) |  |  | OK
| Type: | YSLCY-OZ/JZ | Size [mm2]: |  | 0.5 |  |  | Vo ≤ Vi(min) |  |  | OK
| Description: | Instrument cable | Max Length, Lmax [m]: |  | 2109 |  |  | Po ≤ Pi(min) |  |  | OK
|  |  | Capacitance Core/Core, Ci [nF/km] |  | 135
|  |  | Capacitance Core/Braid, Ci [nF/km] |  | 185 |  |  | Ci(tot) [nF] |  |  | 479.7975
|  |  | Inductance, Li [mH/km]: |  | 0.65 |  |  | Li(tot) [mH] |  |  | 1.3709
|  |  | Resistance [Ώkm/wire]: |  | 39
|  |  | The circuit is approved for gas group: IIC |  |  |  |  | "(min)" er laveste værdi af instru-
menterne i transmitter data
Ui [V] | Maximum voltage that can be applied to the intrinsically safe circuits.
li [mA] | Maximum current that can be applied to the intrinsically safe circuits.
Pi [mW] | Maximum input power in an intrinsically safe circuit that can be dissipated without invalidating intrinsic safety.
Ri [Ώ] | Resistance in the intrinsically safe circuits.
Ci [nF] | Total equivalent internal capacitance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Li [mH] | Total equivalent internal inductance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Uo [V] | Maximun output voltage in an intrinsically safe circuit that can appear under open-circuit conditions.
lo [mA] | Maximum current in an intrinsically safe circuit that can be taken from the connection facilities.
Po [mW] | Maximum electrical power in an intrinsically safe circuit that can be taken from the apparatus.
Ro [Ώ] | Maximum load resistance.
Co [nF] | Maximum capitance in an intrinsically safe circuit that can be connected to the connection facilities.
Lo [mH] | Maximum inductance in an intrinsically safe circuit that can be connected to the connection facilities.

## 30851
Loop id: KA HB 8 04 30851
| Manufacture | Type | Description | Certficate | Authority | Ui [V] | li [mA] | Pi [mW] | Ri [Ώ] | Ci [nF] | Li [mH]
TRANSMITTER DATA | Endress+Hauser | DC11TEN + FEC12 | 2-Wire Transmitter | KEMA 97ATEX4493 | KEMA | 30 | 120 | 1000 |  | 0 | 0
| Manufacture | Type | Description | Certficate | Authority | Uo [V] | lo [mA] | Po [mW] | Ro [Ώ] | Co [nF] | Lo [mH]
BARRIER DATA | R. STAHL | 9461/12-08-11/ -21 | Analog Input | PTB 99 ATEX 2175 | PTB | 26.2 | 91 | 591 |  | 44 | 2
[10 empty] | 58 | 1
[10 empty] | 73 | 0.5
[10 empty] | 97 | 0.2
CABLE DATA | Manufacture: | Coferro | Wires: |  | 2 |  |  | lo ≤ li(min) |  |  | OK
| Type: | YSLCY-OZ/JZ | Size [mm2]: |  | 0.5 |  |  | Vo ≤ Vi(min) |  |  | OK
| Description: | Instrument cable | Max Length, Lmax [m]: |  | 320 |  |  | Po ≤ Pi(min) |  |  | OK
|  |  | Capacitance Core/Core, Ci [nF/km] |  | 135
|  |  | Capacitance Core/Braid, Ci [nF/km] |  | 185 |  |  | Ci(tot) [nF] |  |  | 72.8
|  |  | Inductance, Li [mH/km]: |  | 0.65 |  |  | Li(tot) [mH] |  |  | 0.208
|  |  | Resistance [Ώkm/wire]: |  | 39
|  |  | The circuit is approved for gas group: IIC |  |  |  |  | "(min)" er laveste værdi af instru-
menterne i transmitter data
Ui [V] | Maximum voltage that can be applied to the intrinsically safe circuits.
li [mA] | Maximum current that can be applied to the intrinsically safe circuits.
Pi [mW] | Maximum input power in an intrinsically safe circuit that can be dissipated without invalidating intrinsic safety.
Ri [Ώ] | Resistance in the intrinsically safe circuits.
Ci [nF] | Total equivalent internal capacitance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Li [mH] | Total equivalent internal inductance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Uo [V] | Maximun output voltage in an intrinsically safe circuit that can appear under open-circuit conditions.
lo [mA] | Maximum current in an intrinsically safe circuit that can be taken from the connection facilities.
Po [mW] | Maximum electrical power in an intrinsically safe circuit that can be taken from the apparatus.
Ro [Ώ] | Maximum load resistance.
Co [nF] | Maximum capitance in an intrinsically safe circuit that can be connected to the connection facilities.
Lo [mH] | Maximum inductance in an intrinsically safe circuit that can be connected to the connection facilities.

## 12345
Loop id: 12345
| Fabrikat | Type | Beskrivelse | Certficat | Myndighed | Ui [V] | li [mA] | Pi [mW] | Ri [Ώ] | Ci [nF] | Li [mH]
TRANSMITTER DATA | Vaisala | HMP363A12BCX1A2BB1A1A2 | 2-Wire Transmitter | PTB 00 ATEX 2112 X | PTB | 28 | 100 | 700 |  | 1 | 0
| Fabrikat | Type | Beskrivelse | Certficat | Myndighed | Uo [V] | lo [mA] | Po [mW] | Ro [Ώ] | Co [nF] | Lo [mH]
BARRIER DATA | R. STAHL | 9461/12-08-11/ -21 | Analog Input | PTB 99 ATEX 2175 | PTB | 26.2 | 91 | 591 |  | 44 | 2
[10 empty] | 58 | 1
[10 empty] | 73 | 0.5
[10 empty] | 97 | 0.2
KABEL DATA | Fabrikat | Coferro | Korer: |  | 2 |  |  | lo ≤ li(min) |  |  | OK
| Type | YSLCY-OZ/JZ | Størrelse [mm2]: |  | 0.5 |  |  | Vo ≤ Vi(min) |  |  | OK
| Beskrivelse | Instrument cable | Max Længde, Lmax [m]: |  | 316 |  |  | Po ≤ Pi(min) |  |  | OK
|  |  | Kapacitans Kore/Kore, Ci [nF/km] |  | 135
|  |  | Kapacitans Kore/Skærm, Ci [nF/km] |  | 185 |  |  | Ci(tot) [nF] |  |  | 72.89
|  |  | Inductans, Li [mH/km]: |  | 0.65 |  |  | Li(tot) [mH] |  |  | 0.2054
|  |  | Resistans [Ώkm/wire]: |  | 39
|  |  | Beregningen er godkendt til installation i gas gruppe: IIC |  |  |  |  | "(min)" er laveste værdi af instru-
menterne i transmitter data
Ui [V] | Den største spænding (vekselspændings topværdi eller jævnspænding), som kan tilføres tilslutningsmidlerne for egensikre strømkredse
uden at forringe egensikkerheden.
li [mA] | Den største strøm (vekselstrøms topværdi eller jævnstrøm), som kan tilføres tilslutningsmidlerne for egensikre strømkredse uden at forringe
egensikkerheden.
Pi [mW] | Den største indgangseffekt i en egensikker strømkreds, som uden at forringe egensikkerheden kan afsættes inde i elektrisk materiel,
når det er forbundet til en ydre strømkilde.
Ri [Ώ] | Den største resistans, som anses for at forekomme på det elektriske materiels ydre tilslutningsmidler.
Ci [nF] | Materiellets samlede ækvivalente indre kapacitans, som anses for at forekomme over materiellets tilslutningsmidler.
Li [mH] | Materiellets samlede ækvivalente indre induktans, som anses for at forekomme på materiellets tilslutningsmidler.
Uo [V] | Den største udgangsspænding (vekselspændings topværdi eller jævnspænding), som kan forekomme i en egensikker strømkreds på
materiellets tilslutningsmidler under tomgangsforhold ved enhver tilført spænding op til den største spænding, herunder Um og Ui.
lo [mA] | Den største strøm (vekselstrøms topværdi eller jævnstrøm), som i en egensikker strømkreds kan trækkes fra materiellets tilslutningsmidler.
Po [mW] | Den største elektriske effekt i en egensikker strømkreds, som kan trækkes fra materiellet.
Ro [Ώ] | Den største resistans i enhver ydre strømkreds, som uden at forringe egensikkerheden er forbundet til det elektriske materiels tilslutningsmidler.
Co [nF] | Den største kapacitans i en egensikker strømkreds, som kan forbindes til materiellets tilslutningsmidler uden at forringe egensikkerheden.
Lo [mH] | Den største værdi af induktans i en egensikker strømkreds, som kan forbindes til materiellets tilslutningsmidler uden at forringe egensikkerheden.
Um [V] | Den største spænding, som kan tilføres tilhørende materiels ikke-egensikre tilslutningsmidler uden at forringe egensikkerheden.