## Sheet2
Loop id:TAG nummer xxxxxxx
| Manufacture | Type | Description | Certficate | Authority | Ui [V] | li [mA] | Pi [mW] | Ri [Ώ] | Ci [nF] | Li [mH]
TRANSMITTER DATA | PR electronics A/S | 5335B | 2-Wire Transmitter | KEMA 03ATEX1537 X | KEMA | 30 | 120 | 840 |  | 1 | 0.01
| Manufacture | Type | Description | Certficate | Authority | Uo [V] | lo [mA] | Po [mW] | Ro [Ώ] | Co [nF] | Lo [mH]
BARRIER DATA | R. STAHL | 9461/12-08-11/ -21 | Analog Input | PTB 99 ATEX 2175 | PTB | 26.2 | 91 | 591 |  | 44 | 2
[10 empty] | 58 | 1
[10 empty] | 73 | 0.5
[10 empty] | 97 | 0.2
CABLE DATA | Manufacture: | Norsk cable | Wires: |  | 2 |  |  | lo ≤ li(min) |  |  | OK
| Type: | RFOU© | Size [mm2]: |  | 0.75 |  |  | Vo ≤ Vi(min) |  |  | OK
| Description: | Instrument cable | Max Length, Lmax [m]: |  | 712.5 |  |  | Po ≤ Pi(min) |  |  | OK
|  |  | Capacitance, Ci [nF/km]: |  | 80 |  |  | Ci(tot) [nF] |  |  | 58
|  |  | Inductance, Li [mH/km]: |  | 0.75 |  |  | Li(tot) [mH] |  |  | 0.54438
|  |  | Resistance [Ώkm/wire]: |  | 24.8
The circuit is approved for gas group: IIC
Ui [V] | Maximum voltage that can be applied to the intrinsically safe circuits.
li [mA] | Maximum current that can be applied to the intrinsically safe circuits.
Pi [mW] | Maximum input power in an intrinsically safe circuit that can be dissipated without invalidating intrinsic safety.
Ri [Ώ] | Resistance in the intrinsically safe circuits.
Ci [nF] | Total equivalent internal capacitance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Li [mH] | Total equivalent internal inductance of the apparatus which is considered as appearing across the connection facilities of the apparatus.
Uo [V] | Maximun output voltage in an intrinsically safe circuit that can appear under open-circuit conditions.
lo [mA] | Maximum current in an intrinsically that can be taken from the connection facilities.
Po [mW] | Maximum electrical power in an intrinsically safe circuit that can be taken from the apparatus.
Ro [Ώ] | Maximum load resistance.
Co [nF] | Maximunm capitance in an intrinsically safe circuit that can be connected to the connection facilities.
Lo [mH] | Maximunm inductance in an intrinsically safe circuit that can be connected to the connection facilities.

## Sheet3
Loop id: Test Tag. nummer
[6 empty] | Max.Allowed Voltage | Max.Allowed Current | Max.Allowed Power | Limited Resistance | Load Capacitance | Load Inductance
| Manufacture | Type | Description | Certficate | Authority | Ui [V] | li [mA] | Pi [mW] | Ri [Ώ] | Ci [nF] | Li [mH]
TRANSMITTER DATA | PR electronics A/S | 5335B | 2-Wire Transmitter | KEMA 03ATEX1537 X | KEMA | 30 | 120 | 840 |  | 1 | 0.01
| Manufacture | Type | Description | Certficate | Authority | Uo [V] | lo [mA] | Po [mW] | Ro [Ώ] | Co [nF] | Lo [mH]
BARRIER DATA | R. STAHL | 9461/12-08-11/ -21 | Analog Input | PTB 99 ATEX 2175 |  | 26.2 | 91 | 591 |  | 320 | 15
[10 empty] | 340 | 2
[10 empty] | 390 | 1
[10 empty] | 470 | 0.5
[10 empty] | 590 | 0.2
[10 empty] | 690 | 0.1
[10 empty] | 750 | 0.05
CABLE DATA | Manufacture: | Norsk cable | Wires: |  | 2 |  |  | lo ≤ li(min) |  |  | OK
| Type: | RFOU© | Size [mm2]: |  | 0.75 |  |  | Vo ≤ Vi(min) |  |  | OK
| Description: | Instrument cable | Max Length, Lmax [m]: |  | 3987.5 |  |  | Po ≤ Pi(min) |  |  | OK
|  |  | Capacitance, Ci [nF/km]: |  | 80 |  |  | Ci(tot) [nF] |  |  | 320
|  |  | Inductance, Li [mH/km]: |  | 0.75 |  |  | Li(tot) [mH] |  |  | 3.0006
|  |  | Resistance [Ώkm/wire]: |  | 24.8
|  | Ui [V] | Maximum voltage that can be applied to the intrinsically safe circuits.
|  | li [mA] | Maximum current that can be applied to the intrinsically safe circuits.
|  | Pi [mW] | Maximum input power in an intrinsically safe circuit that can be dissipated without invalidating intrinsic safety.